DASHBOARD SCOPE DOCUMENT

SSB Energy Monitoring Dashboard — Requirements for Developer Handoff

Covers SSB-3 (32 meters, 3-tier) and SSB-4 (combined meter) — Phase 1

| Prepared For | Prepared By |
| --- | --- |
| Development Team — IoT Energy Monitoring Dashboard | ProtoWiz Private Limited / iBots Academy, Coimbatore, Tamil Nadu |

# 1. Purpose of This Document

This document gives the development team a clear, self-contained scope for the SSB energy monitoring dashboard: what the overview page shows, exactly how the energy meters are structured, and what each supporting module needs to do.

# 2. Dashboard Overview (Founder / Management View)

The Overview page is the site-wide landing screen — the first thing a founder or management-level user sees after login. It's built for a showcase, decision-making view: company-wide statistics at a glance, not per-meter detail. It answers “how is the site doing right now” before anyone drills into a specific building, floor, or meter.

## 2.1 KPI Card Row

- Total Energy (kWh) — summed across all live meters (SSB-3's 32 meters + SSB-4's combined meter).

- Total Power Demand (kW) — current peak load across the site.

- Average Power Factor — mean PF across all active meters.

- Active Meters — count of meters currently reporting vs. total meters installed.

- Each card shows a large headline value with its unit, plus two comparison lines: “vs yesterday” and “vs last month,” each with a percentage and an up/down indicator.

## 2.2 Building & Floor Breakdown

- A donut/pie chart showing SSB-3's consumption split across its 4 floors (Ground, 1st, 2nd, 3rd).

- A bar chart showing consumption by panel/area within the selected floor.

- A simple building-level toggle: SSB-3 vs. SSB-4 (SSB-4 shows as a single combined total, not broken down by floor, since it only has one combined meter in Phase 1).

## 2.3 Consumption Trend

- A date-range picker (start date, end date) with a Query action.

- A bar or line chart of total consumption over the selected range, for the selected building/floor scope.

## 2.4 Ranking Panel

- A ranked list of the top (and optionally bottom) meters by consumption over the selected period, showing rank, meter/panel name, and value.

# 3. Role-Based Dashboard Views

The same underlying data supports three distinct views, each scoped and framed for what that person actually needs to act on — not one generic dashboard shown to everyone.

## 3.1 Founder / Management — Company-Wide Statistics

- Scope: all buildings (SSB-3, SSB-4, and future SSB-1/SSB-2), no operational detail by default.

- Focus: the Section 2 Overview — total consumption, cost/efficiency trend, active-meter health, and the Generator Load Forecast summary (Section 5), framed for a showcase or a review meeting rather than day-to-day monitoring.

- Drill-down is available (can open any building's supervisor view) but the default landing screen stays high-level.

## 3.2 Building Supervisor — Building-Wise Updates

- Scope: only the building(s) assigned to that supervisor (e.g., SSB-3 or SSB-4), not the whole site.

- Focus: floor-wise consumption breakdown, live meter table for that building, and alerts originating from that building — essentially Sections 2.2–2.4 and the Live Data module, pre-filtered to their building.

- Typical use: a daily/shift-start check of “is everything in my building normal,” not a company-wide comparison.

## 3.3 Engineer — Technical / Diagnostic Updates

- Scope: assigned building(s), with a technical rather than a summary framing.

- Focus: meter-level health and status (online/offline, last-reading timestamp), alert acknowledgment and resolution, and running-hours/diagnostic detail per panel — the History Data and Alerts modules are the primary tools here.

- Typical use: troubleshooting a specific meter or panel, not reviewing overall consumption trends.

These three views reuse the same modules (Sections 2, 5, and 6) with different default filters and framing — they are not separate applications. Role and building assignment (Section 11) is what drives which view a user lands on.

# 4. Energy Meter Clarity — Buildings, Floors, Panels, Meters

Everything in the dashboard — every filter, card, and chart — is built on top of this exact structure. This is the single source of truth for what a “meter” means in this system.

## 4.1 SSB-3 — 32 Digital Meters, Floor-Wise

| Floor | Area | Panels | Meters |
| --- | --- | --- | --- |
| Ground | Sewing 4 | PDB-1 (5) + PDB-1 (3) | 8 |
| 1st | Sewing 3 | PDB-14/1 (7) + PDB-14 (1 now, +2 planned) | 8 → 10 |
| 2nd | Sewing 2 | PDB-2AD | 6 |
| 3rd | — | PDB-D1 (5) + panel (4) + oil machine (1) | 10 |

Current total: 32 meters (→ 34 once the 2 planned PDB-14 lines are added).

- Data hierarchy: Building → Floor → Panel → Meter. Every meter belongs to exactly one panel, every panel to exactly one floor, every floor to exactly one building.

- Each meter is read by its own IoT node (Tier 1), collected by that floor's hub (Tier 2), and aggregated by one building-wide substation monitoring hub (Tier 3) before reaching the cloud. The dashboard doesn't need to expose these tiers directly — they only matter for explaining where a “no data” gap could originate.

## 4.2 SSB-4 — Combined Meter Only (Phase 1)

- SSB-4's ground floor has a combined/substation-level digital energy meter for the building as a whole (indicative count 5–10, to be confirmed on site).

- In the dashboard, SSB-4 attaches directly to the Building level — it has no floor or panel breakdown in Phase 1.

## 4.3 Not Live Yet — Model For, Don't Build Yet

- SSB-4 per-machine data: 5–10 different textile machine types per floor, integrated flow-wise (Phase 2).

- SSB-1 and SSB-2: currently analog meters, planned for replacement/addressing later (Phase 2).

- Boiler, compressor, and diesel generator (DG) monitoring — phase to be confirmed.

Recommendation for developers: model Building, Floor, Panel, and Meter as first-class entities now, even though only SSB-3 and SSB-4's combined meter carry live data today. This avoids a schema rework when the Phase 2 items go live.

# 5. Generator Load Forecast — Grid vs. DG

This module answers the specific question management wants at a glance: what are we actually consuming, how much of that can the government (EB/grid) supply, and how much has to come from the diesel generator (DG)?

## 5.1 Core Figures

| Figure | Meaning | Source |
| --- | --- | --- |
| Actual Consumption | Real site demand, measured | SSB-3 (32 meters) + SSB-4 combined meter, live |
| Grid Supply Available | What the government/EB connection can currently supply | Sanctioned/contracted load (configured) or a grid-side meter reading, if installed |
| DG Requirement | Shortfall the generator needs to cover | Calculated: max(0, Actual Consumption − Grid Supply Available) |
| DG Actual Output | What the generator is really delivering | DG monitoring hardware (Phase 2) — not available until then |

## 5.2 What the Module Shows

- A single comparison chart: Actual Consumption vs. Grid Supply Available vs. calculated DG Requirement, over a selectable date range.

- A simple forecast line (based on recent historical trend, e.g. a 7/30-day moving average) projecting expected peak demand for the next day/week — useful for planning DG runtime or fuel, not a precision prediction model.

- A summary card set: today's Actual Consumption, Grid Supply Available, and calculated DG Requirement, each with its unit.

## 5.3 Two-Stage Rollout

- Stage A (available now): Actual Consumption comes from live SSB-3/SSB-4 meters; Grid Supply Available is entered/configured by an admin (sanctioned load or known grid capacity); DG Requirement is calculated from the two. No live generator data yet.

- Stage B (once DG monitoring hardware is installed, Phase 2): DG Actual Output becomes live, so the module can show calculated requirement vs. what the generator actually delivered — closing the loop.

Open item: confirm with the customer whether “Grid Supply Available” will be a manually configured value (sanctioned load) or read live from a grid-side meter — this decides whether Stage A needs any new hardware at all.

# 6. Other Modules

| Module | Purpose |
| --- | --- |
| Login | Authentication and role-based landing page |
| Live Data | Real-time table of every meter's current voltage, current, power, power factor, energy, and running hours, with an online/offline status per meter |
| History Data | Historical trend charts and a data table for a selected building/floor/panel/meter and date range, with export |
| Ranking | Standalone version of the Overview ranking panel, with full filtering — highest or lowest consumption, by meter or by floor |
| Report / Print | Generate and export daily/weekly/monthly consumption reports (PDF/Excel), with a compact summary section (total consumption, peak demand, average PF) |
| Alerts | List of triggered alerts — meter offline, abnormal power factor, over/under-voltage — with timestamp, location, and status (open/acknowledged/resolved) |
| Settings | User/role management, alert threshold configuration, and building/floor/panel/meter configuration |

## 6.1 Live Data

- Filterable by Building → Floor → Panel → Meter.

- Auto-refresh at a set polling interval, with a manual refresh option.

## 6.2 History Data

- Same filter set as Live Data, plus a date-range picker.

- Chart view (trend line/bar per parameter) and a table view, both exportable.

## 6.3 Alerts

- Configurable thresholds per parameter, managed from Settings.

- Each alert references the specific building/floor/panel/meter it came from.

## 6.4 Settings

- Needed early even though SSB-1, SSB-2, and SSB-4's machine-level meters aren't live yet — the building/floor/panel/meter configuration screen is what onboards them later without a schema change.

# 7. KPI Card Specifications

| Card | Value Shown | Comparison |
| --- | --- | --- |
| Total Energy | Sum of kWh across selected scope | vs. yesterday, vs. last month |
| Total Power Demand | Peak kW across selected scope | vs. yesterday, vs. last month |
| Average Power Factor | Mean PF across active meters | vs. yesterday, vs. last month |
| Active Meters | Count of meters currently reporting / total meters | — |
| SSB-4 Combined Consumption | kWh from SSB-4's combined meter(s) | vs. yesterday, vs. last month |
| Grid Supply Available | Configured/measured EB supply capacity | — |
| DG Requirement (Calculated) | max(0, Actual Consumption − Grid Supply Available) | vs. yesterday, vs. last month |

# 8. Chart & Table Specifications

| Chart/Table | Type | Data Scope |
| --- | --- | --- |
| Consumption Trend | Bar or line, date-range selectable | Selected building/floor/meter, by day |
| Consumption by Floor (SSB-3) | Donut | 4 floors, share of total kWh |
| Consumption by Panel/Area | Bar | Per-panel totals within selected floor |
| Meter Ranking | Ranked list | Top/bottom N meters by consumption |
| Live Meter Table | Data table | All meters, live values + status |
| History Data Table | Data table, exportable | Selected scope + date range |
| Grid vs. DG Comparison | Line/area, date-range selectable | Actual Consumption vs. Grid Supply vs. calculated DG Requirement |

# 9. Filters & Controls

- Building: SSB-3, SSB-4 (Phase 2: SSB-1, SSB-2).

- Floor: Ground, 1st, 2nd, 3rd (SSB-3 only; not applicable to SSB-4's combined meter).

- Panel: PDB-1 (x2), PDB-14/1, PDB-14, PDB-2AD, PDB-D1, unnamed 4-line panel, oil machine (SSB-3 3rd floor).

- Meter: individual meter selection within a panel.

- Parameter: Voltage, Current, Power, Power Factor, Energy, Running Hours.

- Date range: start/end date picker with a Query action.

# 10. Data Model Requirements

| Entity | Key Fields | Notes |
| --- | --- | --- |
| Building | id, name (SSB-3, SSB-4, …) | Top of hierarchy |
| Floor | id, building_id, name (Ground/1st/2nd/3rd) | SSB-3 only in Phase 1; SSB-4 has no floor breakdown yet |
| Panel | id, floor_id, name (PDB-1, PDB-14/1, …) | Matches Section 3.1 table |
| Meter | id, panel_id, type (digital/analog), status | 32 meters in SSB-3; SSB-4 combined meter(s) attach directly to Building |
| Reading | meter_id, timestamp, voltage, current, power, power_factor, energy_kwh, running_hours | Time-series; one row per poll interval |
| Alert | id, meter_id, type, threshold, triggered_at, status | Drives the Alerts module |
| User | id, name, role, assigned_buildings | Drives role-based access (Section 11) |

Ingestion path: meter-level IoT node → floor hub → building substation hub → cloud (MQTT/HTTPS over 4G, no Wi-Fi on site) → time-series store → dashboard API. SSB-4's combined meter follows the same path via its own gateway.

# 11. Roles & Access

| Role | Access |
| --- | --- |
| SuperAdmin (Founder / Management) | Full access — all buildings, company-wide statistics, settings, user management (Section 3.1) |
| Admin / Building Supervisor | Full operational access to assigned building(s) only — floor breakdown, live data, alerts, reports (Section 3.2); cannot manage other admins |
| Engineer | Assigned building(s), technical/diagnostic access — meter status, alert acknowledgment/resolution, running-hours detail (Section 3.3); no settings or user management |
| Viewer | Read-only access to assigned building(s)/floor(s); no settings or export |

# 12. Non-Functional Requirements

- Live data refresh: near real-time, aligned to the gateway polling interval (target: under 1 minute per meter).

- Historical data retention: minimum 12 months of time-series data available for trend/history queries.

- Connectivity: dashboard and cloud backend must tolerate the site's 4G-only backhaul (no Wi-Fi) — handle intermittent gaps in incoming data gracefully (e.g., “no data” vs. “zero”).

- Responsive layout: usable on desktop and tablet at minimum.

- Export: CSV/Excel for data tables, PDF for reports.

# 13. Phase 1 vs. Phase 2 Dashboard Scope

| Scope Item | Phase |
| --- | --- |
| SSB-3 — all 32 meters, floor/panel breakdown, 3-tier data | Phase 1 |
| SSB-4 — combined ground-floor meter (building-level only) | Phase 1 |
| Founder/Management, Supervisor, Engineer role-based views | Phase 1 |
| Generator Load Forecast — Stage A (calculated DG requirement) | Phase 1 |
| Generator Load Forecast — Stage B (live DG actual output) | Phase 2 (needs DG monitoring hardware) |
| SSB-4 — per-machine timer-running data (5–10 machines/floor) | Phase 2 |
| SSB-1 / SSB-2 — analog meter data | Phase 2 (pending replacement/addressing) |
| Boiler, compressor, DG monitoring | Phase 2 (to be confirmed) |

# 14. Open Items / Assumptions

- SSB-4's combined meter count (indicatively 5–10) needs on-site confirmation before final data-model sizing.

- Exact alert thresholds (voltage range, PF minimum, offline duration) to be confirmed with the customer before Settings defaults are built.

- User list and role assignments (Founder/Management, Building Supervisor, Engineer) to be confirmed with the customer before access control is finalised.

- Grid Supply Available (Section 5.1) needs a decision: manually configured sanctioned load, or a live grid-side meter reading — affects whether any new hardware is needed for Stage A.

- This document assumes cloud API access for the dashboard team; the underlying IoT hardware/gateway scope is covered separately in the main proposal document.

Contact

ProtoWiz Private Limited | iBots Academy — Coimbatore, Tamil Nadu